Updating Date: 28 / 08 / 2026

MODBUS DATA FORMAT (Document Version: 01/02)

Communication Parameters:

1. Register Length			: 26

2. Word Length (Data Length)	: 8 Bit

3. Parity				: None [Disabled]

4. Stop Bits				: 2

6. Baud Rate				: 9600 bits / second

6. Transmission Mode			: RTU

7. Slave Response Delay		: 750 milli seconds, minimum

| Holding Reg Number | Description | Properties | Details / Range |
| --- | --- | --- | --- |
| 1 | PC SET TEMPERATURE REGISTER | READ / WRITE | 19 to 32 Degree Celcius |
| 2 | PC OPERATING MODE REGISTER | READ / WRITE | Details Mentioned Below |
| 3 | RESET COMMAND FROM PC | READ / WRITE | 1 = Reset Fault, Else Donot Reset Fault |
| 4 | CONTROL OPTION REGISTER | READ / WRITE | 0 = Control From PC, Else from Handset |
| 5 | HANDSET CONTROL TIME | READ / WRITE | 1 to 65535 Minutes |
| 6 | NUMBER OF COMPRESSORS IN THE SYSTEM | READ ONLY | Details Mentioned Below |
| 7 | MODEL TYPE | READ ONLY | Details Mentioned Below |
| 8 | CONTROLLER SET TEMPERATURE REGISTER | READ ONLY | 19 to 32 Degree Celcius |
| 9 | CONTROLLER OPERATING MODE REGISTER | READ ONLY | Details Mentioned Below |
| 10 | FAULT RESETTING CONDITION ACTIVE | READ ONLY | 1 = Reset Fault Active, Else Deactive |
| 11 | RETURN AIR TEMPERATURE | READ ONLY |  |
| 12 | COMPRESSOR 1 RUN HOURS | READ ONLY |  |
| 13 | COMPRESSOR 2 RUN HOURS | READ ONLY |  |
| 14 | BLOWER FAN RUN HOURS | READ ONLY |  |
| 15 | COMPRESSOR STATUS REGISTER | READ ONLY | Details Mentioned Below |
| 16 | BLOWER FAN STATUS REGISTER | READ ONLY | Details Mentioned Below |
| 17 | ALARM STATUS REGISTER | READ ONLY | Details Mentioned Below |
| 18 | SYSTEM FAULT REGISTER | READ ONLY | Details Mentioned Below |
| 19 | ANALOG SENSOR FAULT REGISTER | READ ONLY | Details Mentioned Below |
| 20 | COMPRESSOR 1 FAULT REGISTER | READ ONLY | Details Mentioned Below |
| 21 | COMPRESSOR 2 FAULT REGISTER | READ ONLY | Details Mentioned Below |
| 22 | SUPPLY AIR TEMPERATURE | READ ONLY |  |
| 23 | HUMIDITY 1 | READ ONLY |  |
| 24 | HUMIDITY 1 | READ ONLY |  |
| 25 | COMPRESSOR 1 CURRENT | READ ONLY |  |
| 26 | COMPRESSOR 2 CURRENT | READ ONLY |  |

BIT DETAILS:

The data that is transmitted from Slave controller to Master contains following information:

1. Number of Compressors

If number of compressors is to be changed from PC, PC should write this register in following format:

| D15 | D14 | D13 | D12 | D11 | D10 | D9 | D8 | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| D0 | Description |
| --- | --- |
| 0 | 1 Compressor System |
| 1 | 2 Compressor System |

2. Model Type

| D15 | D14 | D13 | D12 | D11 | D10 | D9 | D8 | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

If model type is to be changed from PC, PC should write this register in following format:

Note: This register should be treated as READ ONLY for this application.

| D0 | Description | Bit Applicable To |
| --- | --- | --- |
| 0 | Bluestar Machine (Common HPLP) | IDU |
| 1 | Carrier Machine (Separate HPLP) |  |

| D1 | Description | Bit Applicable To |
| --- | --- | --- |
| 0 | SPPR Sensed from machine’s 3 Phase Monitoring Module | IDU |
| 1 | SPPR Sensed from External SPPR input Connected to HP1 Input |  |

Note: If value of Holding Register 1 or Holding Register 2 is modified, it is assumed that new machine is configured, and so, run hours of fan and compressors is reset to 0.

| D2 | Description | Bit Applicable To |
| --- | --- | --- |
| 0 | System Without ODU | IDU |
| 1 | System With ODU |  |

3. Compressor Status

| D15 | D14 | D13 | D12 | D11 | D10 | D9 | D8 | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Sr. No. | Bit Name | Bit Value | Description | Bit Applicable To |
| --- | --- | --- | --- | --- |
| 1 | D0 | 0 | COMPRESSOR 1 OFF | IDU and Package |
|  |  | 1 | COMPRESSOR 1 ON |  |
| 2 | D1 | 0 | COMPRESSOR 2 OFF | IDU and Package |
|  |  | 1 | COMPRESSOR 2 ON |  |
| 3 | D2 | 0 | COMPRESSOR 3 OFF | Package |
|  |  | 1 | COMPRESSOR 3 ON |  |

4. Blower Fan Status

| D15 | D14 | D13 | D12 | D11 | D10 | D9 | D8 | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Sr. No. | Bit Name | Bit Value | Description | Bit Applicable To |
| --- | --- | --- | --- | --- |
| 1 | D0 | 0 | BLOWER FAN OFF | Package |
|  |  | 1 | BLOWER FAN ON |  |

In case of IDU machines, following is bit allocation to indicate actual fan speed:

| Sr. No. | D2 | D1 | Description |
| --- | --- | --- | --- |
| 1 | 0 | 0 | Blower Fan Running in Low Speed |
| 2 | 0 | 1 | Blower Fan Running in Medium Speed |
| 3 | 1 | 0 | Blower Fan Running in High Speed |
| 4 | 1 | 1 | Future Use |

5. Alarm Status

| D15 | D14 | D13 | D12 | D11 | D10 | D9 | D8 | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Sr. No. | Bit Name | Bit Value | Description | Bit Applicable To |
| --- | --- | --- | --- | --- |
| 1 | D0 | 0 | ALARM OFF | All Models |
|  |  | 1 | ALARM ON |  |

This register indicates whether system is having any alarm or no. If any alarm is there, this register will have value 1, else it would have value 0.

6. System Fault

| D15 | D14 | D13 | D12 | D11 | D10 | D9 | D8 | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Sr. No. | Bit Name | Bit Value | Description | Bit Applicable To |
| --- | --- | --- | --- | --- |
| 1 | D0 | 0 | SPPR FAULT CLEARED | IDU |
|  |  | 1 | SPPR FAULT EXIST |  |
| 2 | D1 | 0 | BF SPPR FAULT CLEARED | IDU |
|  |  | 1 | BF SPPR FAULT EXIST |  |
| 3 | D2 | 0 | ODU-1 COMM ERROR CLEARED | IDU |
|  |  | 1 | ODU-1 COMM ERROR EXIST |  |
| 4 | D3 | 0 | ODU-2 COMM ERROR CLEARED | IDU |
|  |  | 1 | ODU-2 COMM ERROR EXIST |  |

Note: Bits D1, D2 and D3 are applicable if System with ODU is configured.

7. Analog Sensor Fault Register

| D15 | D14 | D13 | D12 | D11 | D10 | D9 | D8 | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Sr. No. | Bit Name | Bit Value | Description | Bit Applicable To |
| --- | --- | --- | --- | --- |
| 1 | D0 | 0 | RAT OPEN FAULT CLEARED | IDU |
|  |  | 1 | RAT OPEN FAULT EXIST |  |
| 2 | D1 | 0 | SAT OPEN FAULT CLEARED | IDU |
|  |  | 1 | SAT OPEN FAULT EXIST |  |
| 3 | D2 | 0 | HUMIDITY 1 OPEN FAULT CLEARED | IDU |
|  |  | 1 | HUMIDITY 1 OPEN FAULT EXIST |  |
| 3 | D3 | 0 | HUMIDITY 2 OPEN FAULT CLEARED | IDU |
|  |  | 1 | HUMIDITY 2 OPEN FAULT EXIST |  |

8. Blower Fan Fault

| D15 | D14 | D13 | D12 | D11 | D10 | D9 | D8 | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Sr. No. | Bit Name | Bit Value | Description | Bit Applicable To |
| --- | --- | --- | --- | --- |
| 1 | D0 | 0 | BLOWER FAN FAULT EXIST | Package |
|  |  | 1 | BLOWER FAN FAULT CLEARED |  |

9. Compressor 1 Fault

| D15 | D14 | D13 | D12 | D11 | D10 | D9 | D8 | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Sr. No. | Bit Name | Bit Value | Description | Bit Applicable To |
| --- | --- | --- | --- | --- |
| 1 | D0 | 0 | ODU 1 SPPR CLEARED | IDU |
|  |  | 1 | ODU 1 SPPR EXIST |  |
| 2 | D1 | 0 | HP /LP 1 FAULT CLEARED | AIRCOOL |
|  |  | 1 | HP/LP 1 FAULT EXIST |  |
| 3 | D2 | 0 | HP 1 FAULT CLEARED | SAPERATE HP & LP |
|  |  | 1 | HP 1 FAULT EXIST |  |
| 4 | D3 | 0 | LP 1 FAULT CLEARED | SAPERATE HP & LP |
|  |  | 1 | LP 1 FAULT EXIST |  |
| 5 | D4 | 0 | ODU 1 OVERLOAD CLEARED | IDU |
|  |  | 1 | ODU 1 OVERLOAD EXIST |  |
| 6 | D5 | 0 | ODU 1 UNDERLOAD CLEARED | IDU |
|  |  | 1 | ODU 1 UNDERLOAD EXIST |  |

D1 bit would be used for Bluestar machines, D2 and D3 bits would be used for Carrier machines.

10. Compressor 2 Fault

| D15 | D14 | D13 | D12 | D11 | D10 | D9 | D8 | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Sr. No. | Bit Name | Bit Value | Description | Bit Applicable To |
| --- | --- | --- | --- | --- |
| 1 | D0 | 0 | ODU 2 SPPR CLEARED | IDU |
|  |  | 1 | ODU 2 SPPR EXIST |  |
| 2 | D1 | 0 | HP /LP 2 FAULT CLEARED | AIRCOOL |
|  |  | 1 | HP/LP 2 FAULT EXIST |  |
| 3 | D2 | 0 | HP 2 FAULT CLEARED | SAPERATE HP & LP |
|  |  | 1 | HP 2 FAULT EXIST |  |
| 4 | D3 | 0 | LP 1 FAULT CLEARED | SAPERATE HP & LP |
|  |  | 1 | LP 2 FAULT EXIST |  |
| 5 | D4 | 0 | ODU 2 OVERLOAD CLEARED | IDU |
|  |  | 1 | ODU 2 OVERLOAD EXIST |  |
| 6 | D5 | 0 | ODU 2 UNDERLOAD CLEARED | IDU |
|  |  | 1 | ODU 2 UNDERLOAD EXIST |  |

D1 bit would be used for Bluestar machines, D2 and D3 bits would be used for Carrier machines.

11.  Operating Mode

| D15 | D14 | D13 | D12 | D11 | D10 | D9 | D8 | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Sr. No. | Bit Name | Bit Value | Description | Bit Applicable To |
| --- | --- | --- | --- | --- |
| 1 | D0 | 0 | OFF MODE | IDU |
|  |  | 1 | ON MODE |  |
| 2 | D5 | 0 | FAN MODE |  |
|  |  | 1 | COOL MODE |  |

| Sr. No. | D2 | D1 | Description |
| --- | --- | --- | --- |
| 1 | 0 | 0 | Fan Speed: Low |
| 2 | 0 | 1 | Fan Speed: Medium |
| 3 | 1 | 0 | Fan Speed: High |
| 4 | 1 | 1 | Future Use |

12. Fault Resetting Condition Active:

If, any fault exists, and, in case fault could be reseted on controller side, controller will write this register as 1, else this register would be 0.

Note: PC should check value of this register and should RESET fault if value of this register is 1.

13. Reset Command from PC:

For resetting any fault from PC, this register should be written as 1. Else it should be written as 0.