Suman Electronics AC Controller

BMS Integration Reference Document

Modbus RTU via RS485 | Document Version: 01/02 | Project: Unimation BMS

# 1. Overview

The Suman Electronics AC Controller is a central plant air conditioning controller that manages compressors, blower fans, and AC operating modes. It communicates with our RS485 Meter Node via the BMS PORT on the INPUT BOX using Modbus RTU protocol.

The controller supports up to 2 compressors (or 3 on Package machines), blower fan control with High/Medium/Low speeds, Cool/Fan/Off operating modes, and set temperature range of 19–32°C.

# 2. Communication Parameters

| Parameter | Value |
| --- | --- |
| Protocol | Modbus RTU |
| Baud Rate | 9600 bps |
| Data Bits | 8 |
| Parity | None |
| Stop Bits | 2 |
| Slave Response Delay | 750ms minimum |
| Function Code (Read) | FC03 — Read Holding Registers |
| Function Code (Write) | FC06 — Write Single Register |
| Register Count | 26 registers (read all in one FC03 transaction) |
| BMS Connection | A, B, GND terminals on INPUT BOX |

NOTE: 2 stop bits are required. Most UART implementations tolerate 1 stop bit but this is not spec-compliant.

# 3. Complete Register Map

| Reg # | Description | R/W | Range / Details |
| --- | --- | --- | --- |
| 1 | PC Set Temperature | R/W | 19 to 32°C |
| 2 | PC Operating Mode | R/W | See Section 5 — mode/fan speed bits |
| 3 | Reset Command from PC | R/W | 1=Reset fault. Write ONLY when Reg 10=1. Auto-clears. |
| 4 | Control Option | R/W | 0=PC control, 1=Handset control |
| 5 | Handset Control Time | R/W | 1 to 65535 minutes |
| 6 | Number of Compressors | R only | D0: 0=1 compressor, 1=2 compressors. READ ONLY from PC. |
| 7 | Model Type | R only | D0=machine type, D1=SPPR type, D2=ODU present. READ ONLY from PC. |
| 8 | Controller Set Temperature | R only | 19 to 32°C (value set on handset) |
| 9 | Controller Operating Mode | R only | Actual operating mode — same bit format as Reg 2 |
| 10 | Fault Resetting Condition Active | R only | 1=fault can be reset by PC, 0=cannot |
| 11 | Return Air Temperature (RAT) | R only | Raw value ÷ 10 = °C (e.g. 271 = 27.1°C). 0 on sensor fault. |
| 12 | Compressor 1 Run Hours | R only | 16-bit integer hours. EEPROM-backed. Rolls over at 65535. |
| 13 | Compressor 2 Run Hours | R only | 16-bit integer hours. EEPROM-backed. |
| 14 | Blower Fan Run Hours | R only | 16-bit integer hours. EEPROM-backed. |
| 15 | Compressor Status | R only | D0=C1 on/off, D1=C2 on/off, D2=C3 on/off (Package only) |
| 16 | Blower Fan Status | R only | Package: D0=fan on/off. IDU: D1/D2=speed (ignore D0). |
| 17 | Alarm Status | R only | D0=alarm present. D1-D15 always 0. |
| 18 | System Fault | R only | D0=SPPR, D1=BF SPPR, D2=ODU1 comm, D3=ODU2 comm |
| 19 | Analog Sensor Fault | R only | D0=RAT open, D1=SAT open, D2=Humidity1 open, D3=Humidity2 open |
| 20 | Compressor 1 Fault | R only | D0=ODU1 SPPR, D1=HP/LP1(Bluestar), D2=HP1(Carrier), D3=LP1(Carrier), D4=Overload, D5=Underload |
| 21 | Compressor 2 Fault | R only | Same pattern as Reg 20 for Compressor 2 |
| 22 | Supply Air Temperature (SAT) | R only | Raw value ÷ 10 = °C. 0 on sensor fault. |
| 23 | Humidity 1 | R only | Raw integer % (52 = 52%). Requires Suman-supplied sensor on HUM1 port. |
| 24 | Humidity 2 | R only | Raw integer % (52 = 52%). Requires Suman-supplied sensor on HUM2 port. |
| 25 | Compressor 1 Current | R only | Valid ONLY when ODU configured. Scaling not confirmed — send raw. |
| 26 | Compressor 2 Current | R only | Valid ONLY when ODU configured. Scaling not confirmed — send raw. |

# 4. Key Terms Explained

## 4.1 SPPR — Single Phase Preventer Relay

SPPR is a power protection device that monitors the 3-phase electrical supply to the AC compressor motor. It cuts power to the compressor if any of the following conditions occur:

• Phase failure — one of the 3 phases drops out

• Phase reversal — phases connected in wrong sequence (motor runs backwards)

• Phase imbalance — voltage difference between phases exceeds threshold

• Under-voltage or over-voltage on any phase

Running a 3-phase compressor motor on 2 phases causes massive current draw and burns out motor windings within seconds. SPPR cuts power before damage occurs.

Two SPPR types (set by DIP switch):

Built-in SPPR: SPPR circuitry is inside the Suman controller itself.

External SPPR: Separate SPPR relay module wired into the circuit. Controller reads its output contact.

## 4.2 HP — High Pressure

The High Pressure switch is a safety sensor on the refrigerant circuit on the high pressure side (between compressor outlet and condenser). It trips when refrigerant pressure exceeds the safe limit.

Common causes: blocked/dirty condenser coil, failed condenser fan, refrigerant overcharge, high ambient temperature.

Fault appears as HP1 Trip or HP2 Trip on controller display.

## 4.3 LP — Low Pressure

The Low Pressure switch is a safety sensor on the low pressure side (between evaporator and compressor inlet). It trips when refrigerant pressure drops below safe limit.

Common causes: refrigerant leak/undercharge, iced evaporator coil, blocked expansion valve, choked return air filter.

## 4.4 IDU vs Package Machine

IDU (Indoor Ductable Unit): The controller manages a separate indoor unit with compressors in an external ODU.

Package Machine: All-in-one unit with compressors inside. No separate ODU.

## 4.5 ODU — Outdoor Unit

The ODU houses the compressors and condenser in IDU systems. It communicates with the INPUT BOX controller digitally. When ODU is present:

• Reg 18 D2/D3 (ODU comm errors) become relevant

• Reg 20/21 D0 (ODU SPPR), D4 (overload), D5 (underload) become relevant

• Reg 25/26 (compressor currents) become valid

# 5. Register Bit Definitions

## 5.1 Operating Mode Register (Reg 2 — Write, Reg 9 — Read)

NOTE: All undefined bits (D3, D4, D6-D15) MUST be written as 0. Non-zero on undefined bits causes controller to IGNORE the command.

| Bit | Function | Value 0 | Value 1 |
| --- | --- | --- | --- |
| D0 | Power | OFF | ON |
| D1 | Fan Speed LSB | See D2:D1 table below |  |
| D2 | Fan Speed MSB | See D2:D1 table below |  |
| D3 | Undefined | Must be 0 | Must be 0 |
| D4 | Undefined | Must be 0 | Must be 0 |
| D5 | Mode | Fan mode | Cool mode |
| D6-D15 | Undefined | Must be 0 | Must be 0 |

| D2 | D1 | Fan Speed |
| --- | --- | --- |
| 0 | 0 | Low |
| 0 | 1 | Medium |
| 1 | 0 | High |
| 1 | 1 | Future use — do not use |

| Mode | Register 2 Value | Hex |
| --- | --- | --- |
| OFF | 0b0000000000000000 | 0x0000 |
| Fan, Low speed | 0b0000000000000001 | 0x0001 |
| Fan, Medium speed | 0b0000000000000011 | 0x0003 |
| Fan, High speed | 0b0000000000000101 | 0x0005 |
| Cool, Low speed | 0b0000000000100001 | 0x0021 |
| Cool, Medium speed | 0b0000000000100011 | 0x0023 |
| Cool, High speed | 0b0000000000100101 | 0x0025 |

## 5.2 Model Type Register (Reg 7 — Read Only)

| Bit | Function | Value 0 | Value 1 |
| --- | --- | --- | --- |
| D0 | Machine type | Bluestar (common HP/LP input) | Carrier (separate HP/LP inputs) |
| D1 | SPPR type | Built-in SPPR | External SPPR |
| D2 | ODU present | No ODU (system without ODU) | ODU present (system with ODU) |
| D3-D15 | Reserved | Always 0 | Always 0 |

## 5.3 Compressor Status Register (Reg 15 — Read Only)

| Bit | Function | Value 0 | Value 1 | Applicable To |
| --- | --- | --- | --- | --- |
| D0 | Compressor 1 | OFF | ON | IDU and Package |
| D1 | Compressor 2 | OFF | ON | IDU and Package |
| D2 | Compressor 3 | OFF | ON | Package machines only |

## 5.4 Blower Fan Status Register (Reg 16 — Read Only)

NOTE: D0 is only valid for Package machines. For IDU machines, ignore D0 and read D1/D2 for fan speed.

| Bit | Function | Value 0 | Value 1 | Applicable To |
| --- | --- | --- | --- | --- |
| D0 | Fan on/off | OFF | ON | Package machines ONLY |
| D1 | Fan speed LSB | See D2:D1 table |  | IDU machines |
| D2 | Fan speed MSB | See D2:D1 table |  | IDU machines |

## 5.5 Alarm Status Register (Reg 17 — Read Only)

| Bit | Function | Value 0 | Value 1 |
| --- | --- | --- | --- |
| D0 | Alarm | No alarm | Alarm present |
| D1-D15 | Reserved | Always 0 | Always 0 |

## 5.6 System Fault Register (Reg 18 — Read Only)

| Bit | Function | Value 0 | Value 1 | Applicable To |
| --- | --- | --- | --- | --- |
| D0 | SPPR Fault | Cleared | Fault exists | IDU |
| D1 | BF SPPR Fault | Cleared | Fault exists | IDU with ODU |
| D2 | ODU 1 Comm Error | Cleared | Error exists | IDU with ODU |
| D3 | ODU 2 Comm Error | Cleared | Error exists | IDU with ODU |

## 5.7 Analog Sensor Fault Register (Reg 19 — Read Only)

| Bit | Function | Value 0 | Value 1 |
| --- | --- | --- | --- |
| D0 | RAT Thermistor | OK | Open fault |
| D1 | SAT Thermistor | OK | Open fault |
| D2 | Humidity 1 Sensor | OK | Open fault |
| D3 | Humidity 2 Sensor | OK | Open fault |

## 5.8 Compressor 1 Fault Register (Reg 20 — Read Only)

| Bit | Function | Value 0 | Value 1 | Applicable To |
| --- | --- | --- | --- | --- |
| D0 | ODU 1 SPPR | Cleared | Fault exists | IDU with ODU |
| D1 | HP/LP 1 (combined) | Cleared | Fault exists | Bluestar machines |
| D2 | HP 1 (separate) | Cleared | Fault exists | Carrier machines |
| D3 | LP 1 (separate) | Cleared | Fault exists | Carrier machines |
| D4 | ODU 1 Overload | Cleared | Fault exists | IDU with ODU |
| D5 | ODU 1 Underload | Cleared | Fault exists | IDU with ODU |

Compressor 2 Fault Register (Reg 21) follows the same bit pattern for Compressor 2 / ODU 2.

# 6. DIP Switch Configuration

DIP switches configure the controller hardware at installation time. These settings cannot be changed via Modbus from the PC. The node reads the resulting configuration from Reg 6 and Reg 7 after power-on.

## 6.1 INPUT BOX DIP Switches

Switch 3 is the master switch — it changes the meaning of Switches 2 and 4.

| Switch 3 | System Type |
| --- | --- |
| ON | System with ODU |
| OFF | System without ODU |

Without ODU (Switch 3 = OFF):

| Switch | ON | OFF |
| --- | --- | --- |
| Switch 1 | 1 Compressor system | 2 Compressor system |
| Switch 2 | External SPPR | Built-in SPPR |
| Switch 3 | System with ODU | System without ODU |
| Switch 4 | Carrier (separate HP/LP) | Bluestar (common HP/LP) |

With ODU (Switch 3 = ON):

| Switch | ON | OFF |
| --- | --- | --- |
| Switch 1 | 1 Compressor system | 2 Compressor system |
| Switch 2 | 3-phase blower fan | Single-phase blower fan |
| Switch 3 | System with ODU | System without ODU |
| Switch 4 | Unused | Unused |

## 6.2 ODU BOX DIP Switches (only when ODU is present)

| Switch | ON | OFF |
| --- | --- | --- |
| Switch 1 | ODU Address: 2 | ODU Address: 1 |
| Switch 2 | Unused | Unused |
| Switch 3 | 3-phase ODU | Single-phase ODU |
| Switch 4 | Carrier (separate HP/LP) | Bluestar (common HP/LP) |

# 7. Fault Reset Procedure

The fault reset sequence must follow this exact order:

Step 1: Read Reg 10 (FAULT_RESET_ACTIVE). If value = 0, do NOT attempt reset — no clearable fault exists.

Step 2: If Reg 10 = 1, write 1 to Reg 3 (RESET_COMMAND).

Step 3: Controller auto-clears Reg 3. Do NOT write 0 back — the controller handles this.

Step 4: Wait for next poll cycle. Read fault registers to confirm fault was cleared.

NOTE: Writing Reg 3 = 1 when Reg 10 = 0 is silently ignored by the controller.

# 8. Control Option (Handset vs PC)

By default the handset controls the AC. When the cloud wants to control:

Take PC control: Write Reg 4 = 0. Then write Reg 1 (temperature) and/or Reg 2 (mode).

Return to handset: Write Reg 4 = 1. Optionally write Reg 5 (handset control time in minutes) to auto-return to PC after that duration.

NOTE: When switching to PC control (Reg 4 = 0), write Reg 4 FIRST before writing Reg 1 or Reg 2. Otherwise the handset may reject the commands.

NOTE: Writing Reg 1 or Reg 2 resets compressor and fan run hours (Reg 12, 13, 14) on the controller. The cloud must be aware of this side effect.

# 9. Temperature Decoding

Registers 11 (RAT) and 22 (SAT) return raw values scaled by 10.

Formula: Temperature (°C) = Register Value ÷ 10

Example: Register reads 271 → 271 ÷ 10 = 27.1°C

Fault condition: Returns 0 when sensor is disconnected or thermistor is open (check Reg 19 D0/D1)

The node sends the raw register value to the cloud. The cloud applies the ÷10 scaling before display.

# 10. BMS Wiring Connection

The RS485 node connects to the BMS PORT on the INPUT BOX:

| Terminal | Connect To | Notes |
| --- | --- | --- |
| A | RS485 A (non-inverting) | From node RS485 A terminal |
| B | RS485 B (inverting) | From node RS485 B terminal |
| GND | Common ground | Shared ground between node and controller |

NOTE: The BMS PORT is a dedicated RS485 port — do not connect to the J2 HANDSET port.

# 11. Firmware Integration Notes

| Topic | Detail |
| --- | --- |
| Read strategy | Single FC03 read of all 26 registers in one transaction (Reg 1-26) |
| Write strategy | FC06 (Write Single Register) per register. Write Reg 4 first if changing control option. |
| Polling frequency | Every publishPeriod (default 120s). Staggered across poll cycle. |
| Event-driven push | Immediate push when alarm_status, system_fault, comp1_fault, or comp2_fault changes (any direction) |
| Fault reset guard | Read Reg 10 before writing Reg 3. Skip reset if Reg 10 = 0. |
| Mode write safety | Mask operating_mode with 0x0027 before writing. Undefined bits must be 0. |
| Temperature decoding | Cloud divides raw value by 10. Node sends raw. |
| Current registers | Only valid when ODU configured (Reg 7 D2 = 1). Send raw regardless. |
| Fan D0 on IDU | Reg 16 D0 is only valid for Package machines. For IDU, read D1/D2 only. |
| Run hours persistence | EEPROM-backed on controller, saved every 30 min. Rolls over at 65535. |
| Humidity sensors | Requires Suman-supplied sensors on HUM1/HUM2 ports. Check Reg 19 D2/D3 before displaying. |
| Compressor current scaling | Scaling factor not confirmed by manufacturer. Send raw value. |