Suman Electronics AC Controller

Field Installation Guide

Addendum to BMS Integration Reference Document | Project: Unimation BMS

# 12. Field Installation Guide

This section is intended for field technicians installing and commissioning the Suman Electronics AC Controller with the Unimation BMS RS485 Node.

## 12.1 Tools and Materials Required

| Item | Details |
| --- | --- |
| RS485 cable (twisted pair) | Min 0.5mm² shielded twisted pair. Max run length 1200m at 9600 baud. |
| Screwdriver (flathead) | For terminal block connections on INPUT BOX |
| Multimeter | To verify RS485 line voltage and continuity |
| Laptop / mobile with BMS app | To send commissioning commands after wiring |
| Suman controller manual | For reference during address setting |

## 12.2 Pre-Installation Checklist

☐  Confirm DIP switch settings with site engineer before powering on

☐  Confirm number of compressors at this installation (1 or 2)

☐  Confirm machine brand (Bluestar / Carrier) — determines HP/LP DIP switch

☐  Confirm if ODU is present at this installation

☐  Assign a unique Modbus slave address for this controller (1-247, different from all other devices on the bus)

☐  Note the assigned slave address — needed for cloud commissioning step

## 12.3 Step 1 — Configure DIP Switches

⚠ WARNING: Power OFF the controller before changing DIP switches.

Set the DIP switches on the INPUT BOX according to the installation type. Switch 3 must be set first.

Common installation — 2 compressors, Bluestar, no ODU:

| Switch | Position | Reason |
| --- | --- | --- |
| Switch 1 | OFF | 2 compressor system |
| Switch 2 | OFF | Built-in SPPR |
| Switch 3 | OFF | No ODU |
| Switch 4 | OFF | Bluestar machine (common HP/LP) |

Common installation — 2 compressors, Carrier, no ODU:

| Switch | Position | Reason |
| --- | --- | --- |
| Switch 1 | OFF | 2 compressor system |
| Switch 2 | OFF | Built-in SPPR |
| Switch 3 | OFF | No ODU |
| Switch 4 | ON | Carrier machine (separate HP/LP) |

NOTE: After changing DIP switches, power ON the controller and verify the correct configuration is reflected in Register 6 and Register 7 via BMS.

## 12.4 Step 2 — Wire RS485 Connection

⚠ WARNING: Do not connect RS485 wiring while either the controller or the RS485 node is powered on.

Connect the RS485 cable between the Unimation RS485 Node and the BMS PORT on the Suman Electronics INPUT BOX:

| RS485 Node Terminal | Suman INPUT BOX Terminal | Wire Color (suggested) |
| --- | --- | --- |
| RS485 A (+) | A | Yellow |
| RS485 B (-) | B | Blue |
| GND | GND | Black |

NOTE: Do NOT connect to the J2 HANDSET port — this is for the LCD handset only.

NOTE: If multiple devices share the RS485 bus, use a daisy-chain topology (not star). Terminate the bus with a 120Ω resistor at each end.

## 12.5 Step 3 — Set Modbus Slave Address

The slave address must be set on the controller within 15 seconds of powering on. Follow this procedure:

Step 1: Power on the controller

Switch on power to the Suman AC controller.

Step 2: Enter address setting mode (within 15 seconds)

Press AC MODE key and RESET key simultaneously and hold continuously for 5 seconds. The display will show ADDRESS SETTING with the current slave address blinking.

Step 3: Change the address

Press UP or DN key to change the slave address. Valid range: 1 to 247. Choose an address that is unique on the RS485 bus.

Step 4: Save the address

Press RESET key to save. The display returns to main screen.

Step 5: Record the address

Note the assigned slave address — you will need to enter it in the BMS cloud portal during commissioning.

NOTE: If you miss the 15-second window, power cycle the controller and repeat from Step 1.

NOTE: The slave address is stored in the controller's non-volatile memory and survives power cycles.

## 12.6 Step 4 — Verify RS485 Communication

After wiring and address setting, verify communication before cloud commissioning:

Step 1: Check LED indicators on RS485 node

TX and RX LEDs should blink briefly when the node attempts to poll. If neither blinks, check wiring and slave address.

Step 2: Check for Modbus timeout errors

If the node reports MODBUS_TIMEOUT in the BMS dashboard, check: (a) RS485 A/B polarity, (b) slave address matches, (c) baud rate is 9600.

Step 3: Verify baud rate on controller

Default baud rate is 9600. If changed previously, re-enter baud rate setting mode (password: 8010) and reset to 9600.

## 12.7 Step 5 — Cloud Commissioning

Once the RS485 node is provisioned to the BMS gateway and communication is verified, add the Suman AC controller from the cloud portal:

Step 1: Log in to BMS cloud portal

Navigate to the site and select the RS485 node that is connected to the Suman AC controller.

Step 2: Add AC Controller

Select "Add Device" → "AC Controller (Suman)". Enter: Slave Address (noted in Step 3), Label (e.g. "FLOOR-2-AC-1").

Step 3: Confirm ACK

The portal should show SUCCESS within 5 seconds. If it shows MODBUS_DEVICE_ALREADY_EXISTS, the slave address was already registered — check if this is a duplicate.

Step 4: Verify live data

After successful commissioning, the portal should show live data within the next poll cycle (up to 120 seconds): RAT, SAT, operating mode, compressor status.

Step 5: Test control

From the portal, send a test command: Turn ON → Fan mode → Medium speed. Verify the AC unit responds and the status update confirms the new mode.

## 12.8 Troubleshooting

| Problem | Possible Cause | Solution |
| --- | --- | --- |
| MODBUS_TIMEOUT | Wrong slave address | Verify address set on controller matches cloud config |
| MODBUS_TIMEOUT | RS485 wiring issue | Check A/B polarity, continuity, and GND connection |
| MODBUS_TIMEOUT | Wrong baud rate | Verify controller is at 9600 baud (default). Reset if needed. |
| MODBUS_TIMEOUT | Bus termination issue | Add 120Ω termination resistors at both ends of RS485 bus |
| RAT/SAT shows 0 | Sensor not connected | Check thermistor wiring on SAT/RAT terminals of INPUT BOX |
| Humidity shows 0 | Sensor not connected | Humidity requires Suman-supplied sensors on HUM1/HUM2 ports |
| Compressor current shows 0 | No ODU configured | Current registers only valid when ODU is present and configured |
| Control commands ignored | Handset in control | Cloud must first set Reg 4 = 0 (PC control) before sending commands |
| HP1/HP2 fault | High pressure trip | Check condenser coil, condenser fan, refrigerant charge |
| LP1/LP2 fault | Low pressure trip | Check refrigerant level, expansion valve, return air filter |
| SPPR fault | Phase power issue | Check 3-phase power supply, phase balance, and SPPR relay |
| Address setting not responding | Missed 15-second window | Power cycle the controller and retry within 15 seconds |

## 12.9 Installer Quick Reference Card

Cut out and keep with the installation for future reference:

SUMAN AC CONTROLLER — FIELD QUICK REFERENCE

RS485: 9600 baud, 8N2, RTU ¦ BMS PORT terminals: A, B, GND Slave address: Set within 15s of power-on ¦ AC MODE + RESET (5s) ¦ Up/Dn to change ¦ RESET to save Baud rate change: AC MODE + RESET (5s) ¦ Password: 8010 ¦ Up/Dn to change ¦ RESET to save Fault reset: Only when Reg 10 = 1. Write Reg 3 = 1. Auto-clears. Temperature: Register value ÷ 10 = °C (e.g. 271 = 27.1°C) PC control: Write Reg 4 = 0 FIRST, then write Reg 1 (temp) / Reg 2 (mode) Mode values: OFF=0x0000 ¦ Fan Low=0x0001 ¦ Fan Med=0x0003 ¦ Fan High=0x0005 ¦ Cool Low=0x0021 ¦ Cool Med=0x0023 ¦ Cool High=0x0025